## Sheet1
Requirement | Name | Body | System Requirement Link | Category | Low Level Requirement Link | Requirement Level
HLR_0010 | Starting display software | Upon execution of the Tunnel lighting system software, the software shall read the Tunnel.ini file and query the user for an input. Configuration files will provide the appropriate data for the example configuration of the system, as described in the document “Tunnel Lighting Control System Overview”. | SYS_0020 | Configuration, Startup | LLR_0100, LLR_0110, LLR_0270, LLR_0440 | HLR
HLR_0020 | Input option photometer nominal range | The software shall allow a real number value in the range 4-20 mAmps to be input for photometer input | SYS_0010, SYS_0040 | Display, Input, Photometer | LLR_0280 | HLR
HLR_0030 | Input options photometer input out of bounds | The software shall handle out of bound range inputs | SYS_0010, SYS_0040 | Display, Input, Photometer | LLR_0282, LLR_0287 | HLR
HLR_0040 | Input options exit | The software shall allow the user to exit the application | SYS_0010 | Display, Input | LLR_0284 | HLR
HLR_0050 | Input options days since cleaning nominal | The software shall allow the user to set the number of days since cleaning | SYS_0010 | Display, Input | LLR_0286 | HLR
HLR_0070 | Input options power failure | The software shall allow the user to invoke all power states | SYS_0010, SYS_0060 | Display, Input | LLR_0288, LLR_0289 | HLR
HLR_0090 | Display total cell demand | In the nominal power state, after entering a nominal range photometer input or nominal days since cleaning, the software shall display Total Cell demand and lumens per metre | SYS_0050 | Display, Output | LLR_0040 | HLR
HLR_0100 | Display Lumens | In the nominal power state, after entering a nominal range photometer input or nominal days since cleaning, the software shall display lumens for each lamp, its power setting, and the lamp ID | SYS_0010 | Display, Output | LLR_0160, LLR_0130 | HLR
HLR_0110 | Cleanliness Factor | A percentage cleanliness factor shall be calculated depending on time elapsed since cleaning. 0% shall represent totally obscurity of the luminaires through the build up of grime; 100% shall represent complete cleanliness. The rate of grime accumulation has been calculated by Waveworks Research Labs, their figures indicate a reduction to 50% over a period of 182 days. | SYS_0030, SYS_0050 | Output calculation, Cleanliness | LLR_0290, LLR_0400, LLR_0410, LLR_0350 | HLR
HLR_0115 | Cleanliness efficiency factor | A “cleanliness efficiency factor” shall be applied on a range from 1 (immediately after cleaning) to 0 (when dirt blanks out all luminaire output) | SYS_0030, SYS_0050 | Output calculation, Cleanliness | LLR_0290, LLR_0400 | HLR
HLR_0120 | Tunnel Lighting Output Demand Calculation | Lighting demand parameters for the tunnel shall be calculated and allocated to each zone | SYS_0030 | Output calculation | LLR_0270, LLR_0490 | HLR
HLR_0125 | Adjust Powered Lighting | Given the photometer input lighting shall be calculated across all zones | SYS_0030 | Output calculation, Zone | LLR_0470, LLR_0450, LLR_0460 | HLR
HLR_0130 | Zone Lighting Formulae | A set of lighting demand straight line formulae shall be calculated to form a contiguous set for all zones | SYS_0030 | Output calculation | LLR_0500, LLR_0510, LLR_0520, LLR_0480 | HLR
HLR_0140 | Zone Lighting Output Demand Calculation | A lighting demand straight line formula shall be calculated for each individual zone | SYS_0030 | Output calculation | LLR_0500, LLR_0510, LLR_0520 | HLR
HLR_0150 | Set Lighting Output Demand Calculation | Lighting demand shall be calculated for each luminaire set | SYS_0030 | Output calculation | LLR_0480 | HLR
HLR_0160 | Lamp Selection | For a particular set, lamps required for inclusion in satisfying current demand levels shall be selected, with efficiency a contributory factor | SYS_0030 | Output calculation, Lamp | LLR_0150, LLR_0160, LLR_0060, LLR_0070, LLR_0080, LLR_0090, LLR_0140, LLR_0140 | HLR
HLR_0170 | Lamp Lighting Output Demand Calculation | Lighting demand shall be calculated for each individual lamp | SYS_0030 | Output calculation, Lamp | LLR_0170, LLR_0180, LLR_0190, LLR_0200 | HLR
HLR_0180 | Tunnel Lighting Output Handling | Commands shall be sent to all lamps to achieve appropriate output overall | SYS_0030, SYS_0130 | Output calculation, Lamp | LLR_0160, LLR_0220, LLR_0230, LLR_0240, LLR_0250, LLR_0260 | HLR
HLR_0190 | Lamp Output Handling | Commands shall be sent to each individual lamp to ensure that appropriate output is achieved in each case | SYS_0030 | Output calculation, Lamp | LLR_0160, LLR_0220, LLR_0230, LLR_0240, LLR_0250, LLR_0260 | HLR
HLR_0200 | Tunnel Lighting Configuration | Configuration facilities shall be provided to facilitate the automatic calculation of the number of lamps which may be positioned in a particular tunnel ceiling area | SYS_0020, SYS_0130 | Configuration, Lamp | LLR_0100, LLR_0110, LLR_0270, LLR_0440 | HLR
HLR_0210 | Exit sign battery drain | The system shall provide data to summarize emergency battery drain imposed by each individual siren & exit sign, and by all such provision in the system as a whole | SYS_0080 | Emergency, Siren Sign, Exit Sign | LLR_0530, LLR_0430, LLR_0360, LLR_0370, LLR_0380, LLR_0390, LLR_0420 | HLR
HLR_0215 | Luminary configuration | Luminaries shall be grouped in sets of one, two, or three depending on where they lie in the tunnel. Lamps within a set can be used in any combination to assist in the optimisation process, which means that the control system need have no concept of the discrete luminaires themselves – only of the sets to which they belong. Luminary grouping will be described in the configuration file | SYS_0020 | Luminary, configuration | LLR_0100, LLR_0110, LLR_0270 | HLR
HLR_0220 | Failed Power Tunnel Lighting Output Calculation | In case of power failure, the power required for all low powered lamps to achieve specified lumens output shall be calculated | SYS_0030, SYS_0060, SYS_0090, SYS_0100 | Output calculation, Lamp | LLR_0030 | HLR
HLR_0230 | Failed Lamp Output Handling | Commands shall be sent to each individual lamp to achieve appropriate output | SYS_0030, SYS_0060 | Output calculation, Lamp | LLR_0160 | HLR
HLR_0231 | Lamps maximum output | A lamp shall provide an output of 120lm/W when used at the maximum output | SYS_0030, SYS_0120 | Output calculation, Lamp | LLR_0120 | HLR
HLR_0232 | Lamp output | Lamp output deterioration shall be computed linearly from 120 lm/W output from each lamp at maximum output, down to 0.2 x 120 / 0.4 = 60 lm/W at 20% output. | SYS_0030, SYS_0110, SYS_0120 | Output calculation, Lamp | LLR_0240, LLR_0250, LLR_0260, LLR_0210 | HLR
HLR_0233 | Minimum lamp output threshold | No lamp shall be used at a required output of less than a configurable minimum percentage of its maximum output. | SYS_0030, SYS_0120 | Output calculation, Lamp | LLR_0240, LLR_0250, LLR_0260 | HLR
HLR_0234 | Lamp extinguishing condition | If for a given lamp the lighting demand drops to levels below the minimum percentage of the its maximum output, the lamp shall be extinguished | SYS_0030, SYS_0120 | Output calculation, Lamp | LLR_0240, LLR_0250, LLR_0260 | HLR
HLR_0235 | Lamp on condition | No lamp shall be turned on unless demand dictates to minimize efficiency overhead and unnecessary toggling | SYS_0030, SYS_0120 | Output calculation, Lamp | LLR_0240, LLR_0250, LLR_0260 | HLR
HLR_0236 | Large lamp use | Larger lamps shall be used to establish the minimum lighting level demanded of any particular set, with a combination of large and small lamps used to respond to fluctuations | SYS_0030, SYS_0120 | Output calculation, Lamp | LLR_0240, LLR_0250, LLR_0260 | HLR
HLR_0237 | Photometer signal conversion | Photometer measurements shall be converted into an output signal of 4-20m/A (directly proportional to the luminance measurement (i.e. 4.0 m/A being given as zero luminance and 20 m/A as 6,500 cd/m2) for signal transmission to the Lighting Control Unit. | SYS_0040 | Photometer, Input | LLR_0470, LLR_0460, LLR_0280. LLR_0282 | HLR
HLR_0340 | System Data Initialisation | All software data shall be stored for management, tracking, and reporting | SYS_0020 | Initialisation, configuration | LLR_0330, LLR_0340 | HLR
HLR_0350 | Mountings Configuration | Mountings shall be configured by dimensions to describe the number of lamps within a mounting | SYS_0020 | Configuration | LLR_0310, LLR_0320 | HLR
HLR_0360 | Cell Configuration and output | Cells output shall be computed based on demand for a given area | SYS_0020, SYS_0030 | Output calculation, Cell | LLR_0050, LLR_0010, LLR_0020, LLR_0040 | HLR